## Definitions
Definitions
Register | Addressable 16-bit pieces of data within a MODBUS device.
Integer | A positive or negative whole number
Concatenate | Concatenate, concatenation, or concat is a term that describes combining a string, text, or other data in a series without any gaps.
NA | Not Applicable
u8 | UnSigned Int8
u16 | UnSigned Int16
u32 | UnSigned Int32
u64 | UnSigned Int64
s8 | Signed Int8
s16 | Signed Int16
FRR | Fast Read Register
MSV | Most Significant Value
LSV | Least Significant Value
PSIG | PSIG (pound-force per square inch gauge) is a unit of pressure relative to the surrounding atmosphere. By contrast, PSIA measures pressure relative to a vacuum (such as that in space).
_H | Suffix identifying the HIGH or first bits of an integer at least 16 bits long.
_L | Suffix identifying the LOW or last bits of an integer at least 16 bits long.

## FRR Decoding Table
Profile | Sensor Name | Data Type | Data Points Presented | Unit | Interpretation | FRR Data
The sensor profile number | Name of the sensor | Describes the base data type being generated by the sensor. *Each row correlates to its own data point | General description of the data present in the FRRs. | Units of measurement for each data point | Describes how to interpret the sensor data as it is presented in Fast Read Registers. Includes the acceptable range of the sensor, and an example of any calculations that may be required to convert the data to usable values. | An example of how the Fast Read Register (FRR) data will be displayed. The FRR values will contain the most relavent information for that sensor. FRRs are able to display multiple registers depending on integer size, and sensor requirements. [FRR_Dat0] - [FRR_Dat1] - [FRR_Dat2] - [FRR_Dat3]
2 | Temperature | s16 | Temperature | Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C | [Temperatue]-[NA]-[NA]-[NA] Example Decimal: [271]-[0]-[0]-[0] Hex: [0x010F]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [65136 to 1250]-[0]-[0]-[0] Hex: [0xFE70 to 0x04E2]-[0x0000]-[0x0000]-[0x0000]
3 | Dry Contact | u8 | Open/Closed | Integer | Default Mode: 0 = Open Loop 1 = Closed Loop | [Open/Closed]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
4 | Water Detect | u8 | Not Present / Present | Integer | Default Mode: 0 = Not Present 1 = Present | [Not Present/Present]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
5 | Activity Detection | u8 | Motion Detected / No Motion Detected | Integer | Default Mode: 0 = No Motion Detected 1 = Motion Detected | [Motion Detected/No Motion Detected]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
9 | Open/Closed | u8 | Open/Closed | Integer | Default Mode: 0 = Open Loop 1 = Closed Loop | [Open/Closed]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
11 | Button | u8 | Checking In / Pressed | Integer | 0 = Checking In 1 = Pressed | [Checking In/Pressed]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
12 | Control | u8 | Relay 1: On/Off; Relay 2: On/Off | Integer | 0 = Both Relays: OFF 1 = Relay 1: ON 2 = Relay 2: ON 3 = Both Relays: ON | [Relay 1: On/Off; Relay 2: On/Off]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
15 | G-Force Snapshot | s16 s16 s16 | X: 0.000 Y: 0.000 Z: 0.000 | G-Force (G) G-Force (G) G-Force (G) | Formula: Divide by 1000 for 3 decimal resolution. Example: 2715 / 1000 = 2.715 Range: -8.000 G to 8.000 G | [X]-[Y]-[Z]-[NA] Example Decimal: [2715]-[0523]-[6025]-[0] Hex: [0x0A9B]-[0x020B]-[0x1789]-[0x0000] Range Decimal: [65472 to 8000]-[65472 to 8000]-[65472 to 8000]-[0] Hex: [0xFF93 to 0x1F40]-[0xFF93 to 0x1F40]-[0xFF93 to 0x1F40]-[0x0000]
16 | Impact | u8 | Force Detected / No Force Detected | Integer | Convert FRR value to binary, each bit represents a different data point generated by the sensor. Definitions for each bit are listed below. Example: 187 = 1011 1011 Byte: hgfe dcba Bit0 (a) - X Polarity: 0 = g+ 1 = g- Bit1 (b) - X Event: 0 = none 1 = happened Bit2 (c) - Y Polarity: 0 = g+ 1 = g- Bit3 (d) - Y Event: 0 = none 1 = happened Bit4 (e) - Z Polarity: 0 = g+ 1 = g- Bit5 (f) - Z Event: 0 = none 1 = happened Bit6 (g) - EA: 0 = none 1 = Global Event happened Bit7 (h) - Internal Communication Problems | [187]-[NA]-[NA]-[NA] Example Decimal: [187]-[0]-[0]-[0] Hex: [0x00BB]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [0 to 255]-[0]-[0]-[0] Hex: [0x0000 to 0x00FF]-[0x0000]-[0x0000]-[0x0000]
21
22 | 0-20 mA Current | u16 | Current | Milliamps (mA) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 744 / 100 = 7.44 mA Range: 0 mA to 24mA | [Milliamps]-[NA]-[NA]-[NA] Example Decimal: [744]-[0]-[0]-[0] Hex: [0x02E8]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [0 to 2400]-[0]-[0]-[0] Hex: [0x0000 to 0x0960]-[0x0000]-[0x0000]-[0x0000]
26
28
32
35 | High Temperature | s16 | Temperature | Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C | [Temperature]-[NA]-[NA]-[NA] Example Decimal: [271]-[0]-[0]-[0] Hex: [0x010F]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [65136 to 1250]-[0]-[0]-[0] Hex: [0xFE70 to 0x04E2]-[0x0000]-[0x0000]-[0x0000]
36
43 | Humidity | s16 s16 | Temperature Relative Humidity | Celsius (C) Relative Humidity (%) | Formula: Divide by 100 for 2 decimal resolution. Formula: Divide by 100 for 2 decimal resolution. Example: 2710 / 100 = 27.10 C, 4555 / 100 = 45.55% Range: -40.0 C to 125.0 C, 00.00% to 100.00% | [Temperature]-[RelativeHumidity]-[NA]-[NA] Example Decimal: [2710]-[4555]-[0]-[0] Hex: [0x0A96]-[0x11CB]-[0x0000]-[0x0000] Range Decimal: [65136 to 1250]-[0 to 10000]-[0]-[0] Hex: [0xFE70 to 0x04E2]-[0x0000 to 0x2710]-[0x0000]-[0x0000]
46 | Low Temperature | s16 | Temperature | Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -200.0 to 162.0 C | [Temperature]-[NA]-[NA]-[NA] Example Decimal: [271]-[0]-[0]-[0] Hex: [0x010F]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [63536 to 1620]-[0]-[0]-[0] Hex: [0xF830 to 0x0654]-[0x0000]-[0x0000]-[0x0000]
56 | H2S | s16 s16 s16 | Temperature H2S Instant H2S TWA | Celsius (C) Parts Per Million (PPM) Parts Per Million (PPM) | Formula: Divide by 10 for 1 decimal resolution. Formula: Divide by 1000 for 1 decimal resolution. Formula: Divide by 1000 for 1 decimal resolution. Example: 271 / 10 = 27.1 C 17800 / 1000 = 17.8 PPM Range: -40.0 C to 125.0 C | [Temperature]-[H2SInstant]-[H2STWA]-[NA] Example Decimal: [271]-[17800]-[2300]-[0] Hex: [0x010F]-[0x4588]-[0x08FC]-[0x0000] Range Decimal: [65136 to 1250]-[0 to 50000]-[0 to 50000]-[0] Hex: [0xFE70 to 0x04E2]-[0x0000 to 0xC350]-[0x0000 to 0xC350]-[0x0000]
59
64 | Voltage Detect 500VAC | u8 | No Voltage Present / Voltage Present | Integer | Default Mode: 0 = No Voltage Present 1 = Voltage Present | [VoltagePresent]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
65 | Water Temperature | s16 | Temperature | Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C | [Temperature]-[NA]-[NA]-[NA] Example Decimal: [271]-[0]-[0]-[0] Hex: [0x010F]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [65136 to 1250]-[0]-[0]-[0] Hex: [0xFE70 to 0x04E2]-[0x0000]-[0x0000]-[0x0000]
67 | Commercial Ultrasonic | u16 | Distance | Centimeters (CM) | Distance from target in CM. Range: 10 CM to 400 CM | [Distance]-[NA]-[NA]-[NA] Example Decimal: [350]-[0]-[0]-[0] Hex: [0x015E]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [10 to 400]-[0]-[0]-[0] Hex: [0x000A to 0x0190]-[0x0000]-[0x0000]-[0x0000]
70 | Resistance | u32 | Resistance | Ohms (Ω) | Data produced by the sensor is in u32 format. 2 out of 4 FRRs are needed to contain this value. Concatenate the FRRs in order to reconstruct the full value. Concatenate: [Resistance0] + [Resistance1] MSV LSV Formula After Concatenate: Divide by 10 for 1 decimal point resolution Example: [37] - [46402] -> Convert to Hexadecimal [0x0025] + [0xB542] = [0x0025B542] Convert Concatenated result back to Decimal 2,471,234 / 10 = 247,123.4 Ω Range: 0 to 250,000.0 Ω | [Resistance0]-[Resistance1]-[NA]-[NA] Example Decimal: [37]-[46402]-[NA]-[NA] Hex: [0x0025]-[0xB542]-[0x0000]-[0x0000] Range Decimal: [0 to 38]-[0 to 65535]-[0]-[0] Hex: [0x0026 to 0xFFFF]-[0x0000 to 0xFFFF]-[0x0000]-[0x0000]
71
72 | 0-5 VDC | u16 | Voltage | Volts (V) | Formula: Divide by 1000 to get 1 decimal point resolution. Example: 3400 / 1000 = 3.4 V Range: 0 V to 5 V | [Volts]-[NA]-[NA]-[NA] Example Decimal: [3400]-[0]-[0]-[0] Hex: [0x0D48]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [0 to 5000]-[0]-[0]-[0] Hex: [0x0000 to 0x1388]-[0x0000]-[0x0000]-[0x0000]
74 | 0-10 VDC | u16 | Voltage | Volts (V) | Formula: Divide by 1000 to get 1 decimal point resolution. Example: 7400 / 1000 = 7.4 V Range: 0 V to 10 V | [Volts]-[NA]-[NA]-[NA] Example Decimal: [7400]-[0]-[0]-[0] Hex: [0x1CE8]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [0 to 10000]-[0]-[0]-[0] Hex: [0x0000 to 0x2710]-[0x0000]-[0x0000]-[0x0000]
75 | Tilt | s16 s16 | Pitch Roll | Degrees (°) Degrees (°) | Formula: Divide by 100 for 2 decimal point resolution. Example: 17518 / 100 = 175.18° Range: -180.00° to 180.00° | [Pitch]-[Roll]-[NA]-[NA] Example Decimal: [16578]-[238]-[0]-[0] Hex: [0x40C2]-[0x00EE]-[0x0000]-[0x0000] Range Decimal: [47536 to 18000]-[47536 to 18000]-[0]-[0] Hex: [0xB9B0 to 0x4650]-[0xB9B0 to 0x4650]-[0x0000]-[0x0000]
78 | Water Rope | u8 | No Water Present / Water Present | Integer | Default Mode: 0 = No Water Present 1 = Water Present | [NoWaterPresent/WaterPresent]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
79 | Pressure 50 | u16 | Pressure | Pounds/Square Inch (PSIG) | Formula: Divide by 10 to get 1 decimal point resolution. Example: 359 / 10 = 35.9 PSI Range: 0 PSI to 50 PSI | [Pressure]-[NA]-[NA]-[NA] Example Decimal: [340]-[0]-[0]-[0] Hex: [0x0167]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [0 to 500]-[0]-[0]-[0] Hex: [0x0000 to 0x01F4]-[0x0000]-[0x0000]-[0x0000]
82 | Pressure 300 | u16 | Pressure | Pounds/Square Inch (PSIG) | Formula: Divide by 10 to get 1 decimal point resolution. Example: 2595 / 10 = 259.5 PSI Range: 0 PSI to 300 PSI | [Pressure]-[NA]-[NA]-[NA] Example Decimal: [2595]-[0]-[0]-[0] Hex: [0x0A23]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [0 to 3000]-[0]-[0]-[0] Hex: [0x0000 to 0x0BB8]-[0x0000]-[0x0000]-[0x0000]
83 | Pressure Custom | u16 | Pressure | Pounds/Square Inch (PSIG) | Formula: Divide by 10 to get 1 decimal point resolution. Example: 359 / 10 = 35.9 PSI Range: 0 PSI to 50 PSI | [Pressure]-[NA]-[NA]-[NA] Example Decimal: [340]-[0]-[0]-[0] Hex: [0x0167]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [0 to 500]-[0]-[0]-[0] Hex: [0x0000 to 0x01F4]-[0x0000]-[0x0000]-[0x0000]
84 | Duct Temperature | s16 | Temperature | Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C | [Temperature]-[NA]-[NA]-[NA] Example Decimal: [271]-[0]-[0]-[0] Hex: [0x010F]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [65136 to 1250]-[0]-[0]-[0] Hex: [0xFE70 to 0x04E2]-[0x0000]-[0x0000]-[0x0000]
86 | Thermocouple | s16 | Temperature | Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -100.0 to 400.0 C | [Temperature]-[NA]-[NA]-[NA] Example Decimal: [271]-[0]-[0]-[0] Hex: [0x010F]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [65436 to 4000]-[0]-[0]-[0] Hex: [0xFF9C to 0x0FA0]-[0x0000]-[0x0000]-[0x0000]
90 | Pulse Counter(64) | u64 | Count | Pulses | Data produced by the sensor is in u64 format. All 4 FRRs are required to store this value. Concatenate the FRRs in order to reconstruct the full value. Concatenate: [Count0]+[Count1]+[Count2]+[Count3] MSV LSV Example: (Decimal) (Hexadecimal) [0]-[1]-[6498]-[43584] ---> [0x0000]-[0x0001]-[0x1962]-[0xAA40] (Individual FRR) (Concatenated) [0x0000]+[0x0001]+[6498]+[43584] = 0x000000011962AA40 --> Decimal 4,720,863,808 is the reconstructed full value Range: 0 to 2^64-1 | [Count0]-[Count1]-[Count2]-[Count3] Example Decimal: [65535]-[65535]-[65535]-[65535] Hex: [0xFFFF]-[0xFFFF]-[0xFFFF]-[0xFFFF] Range Decimal: [0 to 65535]-[0 to 65535]-[0 to 65535]-[0 to 65535] Hex: [0x0000 to 0xFFFF]-[0x0000 to 0xFFFF]-[0x0000 to 0xFFFF]-[0x0000 to 0xFFFF]
92 | Quad Temp | s16 s16 s16 s16 | Temperature Temperature Temperature Temperature | Celsius (C) Celsius (C) Celsius (C) Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C | [Temperature]-[Temperature]-[Temperature]-[Temperature] Example Decimal: [271]-[271]-[271]-[271] Hex: [0x010F]-[0x010F]-[0x010F]-[0x010F] Range Decimal: [65136 to 1250]-[65136 to 1250]-[65136 to 1250]-[65136 to 1250] Hex: [0xFE70 to 0x04E2]-[0xFE70 to 0x04E2]-[0xFE70 to 0x04E2]-[0xFE70 to 0x04E2]
93 | Current Meter 20A | u16 u16 u16 | Avg Current Max Current Min Current | Amps (A) Amps (A) Amps (A) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A Range: 0 A to 50 A *Physical hardware limitations* | [Amps]-[Amps]-[Amps]-[NA] Example Decimal: [1567]-[1567]-[1567]-[0] Hex: [0x061F]-[0x061F]-[0x061F]-[0x0000] Range Decimal: [0 to 5000]-[0 to 5000]-[0 to 5000]-[0] Hex: [0x0000 to 0x1388]-[0x0000 to 0x1388]-[0x0000 to 0x1388]-[0x0000]
94 | Current Meter 150A | u16 u16 u16 | Avg Current Max Current Min Current | Amps (A) Amps (A) Amps (A) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A Range: 0 A to 200 A *Physical hardware limitations* | [Amps]-[Amps]-[Amps]-[NA] Example Decimal: [1567]-[1567]-[1567]-[0] Hex: [0x061F]-[0x061F]-[0x061F]-[0x0000] Range Decimal: [0 to 20000]-[0 to 20000]-[0 to 20000]-[0] Hex: [0x0000 to 0x4E20]-[0x0000 to 0x4E20]-[0x0000 to 0x4E20]-[0x0000]
95 | Vibration Meter | u8 u8 u8 u8 | X Speed Y Speed Z Speed Duty Cycle | Millimeters Per Second (MM/S) Millimeters Per Second (MM/S) Millimeters Per Second (MM/S) Percentage (%) | Formula: Divide by 10 for 1 decimal resolution Formula: Divide by 10 for 1 decimal resolution Formula: Divide by 10 for 1 decimal resolution No calculation required Example: 235 / 10 = 23.5 mm/s Range: 0 to 255, 0 to 255, 0 to 255, 0 to 100 | [XSpeed]-[YSpeed]-[ZSpeed]-[DutyCylce] Example Decimal: [235]-[142]-[38]-[78] Hex: [0x00EB]-[0x008E]-[0x0026]-[0x004E] Range Decimal: [0 to 255]-[0 to 255]-[0 to 255]-[0 to 100] Hex: [0x0000 to 0x00FF]-[0x0000 to 0x00FF]-[0x0000 to 0x00FF]-[0x0000 to 0x0064]
97 | Thermostat | s16 s16 u8 | Temerature Humidity State | Celsius (C) Relative Humidity (%) Integer | Formula: Divide by 100 for 2 decimal resolution. Formula: Divide by 100 for 2 decimal resolution. Covert to Binary to identify what states are active. Each bit corresponds to an individual state. See State/Bit definitions below. Example: 2710 / 10 = 27.10 C, 4555 / 100 = 45.55%, 13 = 0000 1101 (LSV) Bit0 - Heater State 0 = OFF / 1 = ON Bit1 - Cooler State 0 = OFF / 1 = ON Bit2 - Fan State 0 = OFF / 1 = ON Bit3 - Occupancy State 0 = OFF / 1 = ON Bit4 - Fan Override 0 = OFF / 1 = ON Bit5 - Occupied Overried 0 = OFF / 1 = ON Bit6 - Unoccupied Overried 0 = OFF / 1 = ON (MSV) Bit7 - Settings Lockout 0 = OFF / 1 = ON Range: -40.0 C to 85.0 C, 00.00% to 100.00%, 0 to 255 | [Temperature]-[RelativeHumidity]-[State]-[NA] Example Decimal: [2710]-[4555]-[13]-[0] Hex: [0x0A96]-[0x11CB]-[0x000D]-[0x0000] Range Decimal: [0 to 8500]-[0 to 10000]-[0 to 255]-[0] Hex: [0x0000 to 0x2134]-[0x0000 to 0x2710]-[0x0000 to 0x00FF]-[0x0000]
98
100
101 | PIR | u8 | Motion Detected / No Motion Detected | Integer | Default Mode: 0 = No Motion Detected 1 = Motion Detected | [Motion Detected/No Motion Detected]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
102 | Air Quality | u16 u16 u16 | PM 1 PM 2.5 PM 10 | Micrograms/meter cubed (ug/m^3) Micrograms/meter cubed (ug/m^3) Micrograms/meter cubed (ug/m^3) | No conversion required. Range: 0 to 1000 ug/m^3 | [PM1]-[PM2_5]-[PM10]-[NA] Example Decimal: [987]-[567]-[156]-[0] Hex: [0x03DB]-[0x0237]-[0x009C]-[0x0000] Range Decimal: [0 to 1000]-[0 to 1000]-[0 to 1000]-[0] Hex: [0x0000 to 0x03E8]-[0x0000 to 0x03E8]-[0x0000 to 0x03E8]-[0x0000]
103 | Differential Pressure | s16 s16 | Pressure Temperature | Pascals (Pa) Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Formula: Divide by 10 for 1 decimal resolution. Example: 2710 / 10 = 271.0 Pa, 455 / 10 = 45.5 C Range: -500 to 500 Pa, -40.0 C to 125.0 C | [Pressure]-[Temperature]-[NA]-[NA] Example Decimal: [2710]-[455]-[0]-[0] Hex: [0x0A96]-[0x01C7]-[0x0000]-[0x0000] Range Decimal: [65036 to 5000]-[65136 to 1250]-[0]-[0] Hex: [0xFE0C to 0x1388]-[0xFE70 to 0x04E2]-[0x0000]-[0x0000]
105 | Industrial Ultrasonic | u16 | Distance | Centimeters (CM) | Distance from target in CM. Range: 20 CM to 750 CM | [Distance]-[NA]-[NA]-[NA] Example Decimal: [350]-[0]-[0]-[0] Hex: [0x015E]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [10 to 400]-[0]-[0]-[0] Hex: [0x000A to 0x0190]-[0x0000]-[0x0000]-[0x0000]
106 | C02 Meter | s16 s16 | Instant C02 TWA C02 | Parts Per Million (PPM) Parts Per Million (PPM) | Displays C02 in parts per million. Example: C02 Instantaneous: 2710 PPM / C02 TWA: 100 PPM Range: 0 to 10,000 PPM | [Instant_C02]-[TWA_C02]-[NA]-[NA] Example Decimal: [2710]-[100]-[0]-[0] Hex: [0x0A96]-[0x0064]-[0x0000]-[0x0000] Range Decimal: [0 to 10000]-[0 to 10000]-[0]-[0] Hex: [0x0000 to 0x2710]-[0x0000 to 0x2710]-[0x0000]-[0x0000]
107 | Light Meter | u32 u8 | Intensity Light/No Light | Luminescence/unit area (LUX) Integer | Data produced by the sensor is in multiple formats, u32 and u8. The u32 value utilizes 2 out of 4 FRRs in order to display this data. The u8 value is displayed in it's own FRR. To recontruct the original u32 value, concatenate the FRRs in the following order: Concatenate: [Intensity0]+[Intensity1] - [Light/NoLight] - [NA] MSV LSV *Not Concatenated* Formula After Concatenate: Divide by 100 for 2 decimal point resolution Example: [1] - [28995] -> Convert to Hexadecimal [0x0001] + [0x7143] = [0x00017143] Convert Concatenated result back to Decimal 94,531 / 100 = 945.31 LUX Range: 0 - 1000 LUX, 0 = No Light / 1 = Light | [Intensity0]-[Intensity1]-[Light/NoLight]-[NA] Example Decimal: [1]-[28995]-[1]-[NA] Hex: [0x0001]-[0x7143]-[0x0001]-[0x0000] Range Decimal: [0 to 65535]-[0 to 65535]-[0 to 1]-[0] Hex: [0x0000 to 0xFFFF]-[0x0000 to 0xFFFF]-[0x0000 to 0x0001]-[0x0000]
109 | Three Phase 150A | u16 u16 u16 | Phase1 Avg Current Phase2 Avg Current Phase3 Avg Current | Amps (A) Amps (A) Amps (A) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A Range: 0 A to 200 A *Physical hardware limitations for each phase* | [Amps]-[Amps]-[Amps]-[NA] Example Decimal: [1567]-[1567]-[1567]-[0] Hex: [0x061F]-[0x061F]-[0x061F]-[0x0000] Range Decimal: [0 to 20000]-[0 to 20000]-[0 to 20000]-[0] Hex: [0x0000 to 0x4E20]-[0x0000 to 0x4E20]-[0x0000 to 0x4E20]-[0x0000]
111 | Advanced Vibration | s16 u16 u16 u16 | Temperature Vibration - X Vibration - Y Vibration - Z | Celsius (C) mm/s^2 OR mm/s OR mm mm/s^2 OR mm/s OR mm mm/s^2 OR mm/s OR mm | NOTE: Vibration can be measured in Acceleration, Velocity, or Displacement and this will determine the units. Formulas Temperature: Divide by 10 for 1 decimal resolution. Vibration - X: (mm/s^2)*10 OR (mm/s) / 100 OR (mm) / 100 Vibration - Y: (mm/s^2)*10 OR (mm/s) / 100 OR (mm) / 100 Vibration - Z: (mm/s^2)*10 OR (mm/s) / 100 OR (mm) / 100 Example: 271 / 10 = 27.1 C Range: -40 C to 125 C | [Temperature]-[X]-[Y]-[Z] Example Decimal: [271]-[65535]-[65535]-[65535] Hex: [0x010F]-[0xFFFF]-[0xFFFF]-[0xFFFF] Range Decimal: [65136 to 1250]-[0 to 65535]-[0 to 65535]-[0 to 65535] Hex: [0xFE70 to 0x04E2]-[0x0000 to 0cxFFFF]-[0x0000 to 0cxFFFF]-[0x0000 to 0cxFFFF]
113 | Voltage Meter 200VDC | u32 | Voltage | Volts (V) | Data produced by the sensor is in u32 format. 2 out of 4 FRRs are needed to contain this value. Concatenate the FRRs in order to reconstruct the full value. Concatenate: [Voltage0] + [Voltage1] MSV LSV Formula After Concatenate: Divide by 100 for 2 decimal point resolution Example: [0] - [17514] -> Convert to Hexadecimal [0x0000] + [0x446A] = [0x0000446A] Convert Concatenated result back to Decimal 17514 / 100 = 175.14 V Range: 0 - 250 V *Physical hardware limitations* | [Voltage0]-[Voltage1]-[NA]-[NA] Example Decimal: [0]-[17514]-[NA]-[NA] Hex: [0x0000]-[0x446A]-[0x0000]-[0x0000] Range Decimal: [0 to 65535]-[0 to 65535]-[0]-[0] Hex: [0x0000 to 0xFFFF]-[0x0000 to 0xFFFF]-[0x0000]-[0x0000]
114 | Air Velocity | s16 s16 | Velocity Temperature | Meters Per Second (M/S) Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 176 / 10 = 17.6 m/s, 271 / 10 = 27.1 C Range: 0 to 50 m/s, -40.0 C to 125.0 C NOTE: Velocity range will change based on altitude. 0M = 0-30 m/s, 5000M = 0-40 m/s, 8000M = 0-50 m/s | [Velocity]-[Temperature]-[NA]-[NA] Example Decimal: [176]-[271]-[0]-[0] Hex: [0x00B0]-[0x010F]-[0x0000]-[0x0000] Range Decimal: [0 to 500]-[65136 to 1250]-[0]-[0] Hex: [0x0000 to 0x01F4]-[0xFE70 to 0x04E2]-[0x0000]-[0x0000]
116 | C0 Meter | u16 u16 u16 | Temperature Instant C0 TWA C0 | Celsius (C) Parts Per Million (PPM) Parts Per Million (PPM) | Formula: Divide by 10 for 1 decimal resolution. Formula: Divide by 10 for 1 decimal resolution. Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40 to 125 C, 0 to 1000 PPM | [Temperature]-[Instant_C0]-[TWA_CO]-[NA] Example Decimal: [271]-[9821]-[104]-[0] Hex: [0x010F]-[0x265D]-[0x0068]-[0x0000] Range Decimal: [65136 to 1250]-[0 to 10000]-[0 to 10000]-[0] Hex: [0xFE70 to 0x04E2]-[0x0000 to 0x2710]-[0x0000 to 0x2710]-[0x0000]
119 | Car Detect | u8 u16 | Mode Indicator Car Count | Integer Integer | Identifies which mode the sensor is currently operating in. 0 = No Car Detected 1 = Car Detected (Trigger Modes), 2 = Count Mode Counts the numbers of cars detected within a user configured timeframe. Range: 0-2, 0-65535 | [Mode]-[Count]-[NA]-[NA] Example Decimal: [2]-[12]-[0]-[0] Hex: [0x0002]-[0x000C]-[0x0000]-[0x0000] Range Decimal: [0 to 2]-[0 to 65535]-[0]-[0] Hex: [0x0000 to 0x0002]-[0x0000 to 0xFFFF]-[0x0000]-[0x0000]
120 | Current Meter 500A | u16 u16 u16 | Avg Current Max Current Min Current | Amps (A) Amps (A) Amps (A) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A Range: 0 A to 600 A *Physical hardware limitations* | [Amps]-[Amps]-[Amps]-[NA] Example Decimal: [1567]-[1567]-[1567]-[0] Hex: [0x061F]-[0x061F]-[0x061F]-[0x0000] Range Decimal: [0 to 60000]-[0 to 60000]-[0 to 60000]-[0] Hex: [0x0000 to 0xEA60]-[0x0000 to 0xEA60]-[0x0000 to 0xEA60]-[0x0000]
122 | Voltage Meter 500VAC | u16 | Voltage | Volts (V) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 15670 / 100 = 156.70 A Range: 0 A to 600 A *Physical hardware limitations* | [Volts]-[NA]-[NA]-[NA] Example Decimal: [15670]-[0]-[0]-[0] Hex: [0x3D36]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [0 to 60000]-[0]-[0]-[0] Hex: [0x0000 to 0xEA60]-[0x0000]-[0x0000]-[0x0000]
123 | Voltage Detect 200VDC | u8 | No Voltage Present / Voltage Present | Integer | Default Mode: 0 = No Voltage Present 1 = Voltage Present | [VoltagePresent]-[NA]-[NA]-[NA] Example Decimal: [1]-[0]-[0]-[0] Hex: [0x0001]-[0x0000]-[0x0000]-[0x0000]
124 | Propane | s16 u16 | Gas Level Voltage | Percentage (%) Millivolts (mV) | How much gas is remaining in the tank. Hall Effect reading expresed as mV. Formula: Divide by 100 for 2 decimal resolution. Range: 0-100, 0-5000 | [Gas_Level]-[Voltage]-[NA]-[NA] Example Decimal: [78]-[1123]-[0]-[0] Hex: [0x004E]-[0x0463]-[0x0000]-[0x0000] Range Decimal: [0 to 100]-[0 to 5000]-[0]-[0] Hex: [0x0000 to 0x0064]-[0x0000 to 0x1388]-[0x0000]-[0x0000]
126 | Accelerometer Max/Avg | u16 u16 u16 u16 | X Max Y Max Z Max Avg Magnitude | G-Force (G) G-Force (G) G-Force (G) G-Force (G) | Formula: Divide by 1000 for 3 decimal resolution. Example: 7856 / 1000 = 7.856 G Range: 0.000 to 8.000 G | [X_Max]-[Y_Max]-[Z_Max]-[Avg_MAG] Example Decimal: [1264]-[3567]-[7856]-[951] Hex: [0x04F0]-[0x0DEF]-[0x1EB0]-[0x03B7] Range Decimal: [0 to 8000]-[0 to 8000]-[0 to 8000]-[0 to 8000] Hex: [0x0000 to 0x1F40]-[0x0000 to 0x1F40]-[0x0000 to 0x1F40]-[0x0000 to 0x1F40]
129 | Three Phase 500A | u16 u16 u16 | Phase1 Avg Current Phase2 Avg Current Phase3 Avg Current | Amps (A) Amps (A) Amps (A) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A Range: 0 A to 600 A *Physical hardware limitations for each phase* | [Amps]-[Amps]-[Amps]-[NA] Example Decimal: [1567]-[1567]-[1567]-[0] Hex: [0x061F]-[0x061F]-[0x061F]-[0x0000] Range Decimal: [0 to 60000]-[0 to 60000]-[0 to 60000]-[0] Hex: [0x0000 to 0xEA60]-[0x0000 to 0xEA60]-[0x0000 to 0xEA60]-[0x0000]
130 | Accelerometer Tilt Detect | S16 S16 S8 | Pitch Actuation Time State | Degrees milliseconds N/A | Formula: Divide by 100 for 2 decimal resolution. Example: 150 / 100 = 1.50 degrees Range: -179.99 thru +180.00 Actuation Time is in ms. State is used as is and represents the following in Up/Down mode: 0 - Down, 1 - UP, 2 - Stuck State is used as is and represents the following in Delta mode: 0 - not triggered, 1 - delta change triggered | [Future addition]
131 | Filtered Quad Temp | s16 s16 s16 s16 | Temperature Temperature Temperature Temperature | Celsius (C) Celsius (C) Celsius (C) Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C | [Temperatue]-[Temperatue]-[Temperatue]-[Temperatue] Example Decimal: [271]-[271]-[271]-[271] Hex: [0x010F]-[0x010F]-[0x010F]-[0x010F] Range Decimal: [65136 to 1250]-[65136 to 1250]-[65136 to 1250]-[65136 to 1250] Hex: [0xFE70 to 0x04E2]-[0xFE70 to 0x04E2]-[0xFE70 to 0x04E2]-[0xFE70 to 0x04E2]
132 | Filtered Temperature | s16 | Temperature | Celsius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C | [Temperatue]-[NA]-[NA]-[NA] Example Decimal: [271]-[0]-[0]-[0] Hex: [0x010F]-[0x0000]-[0x0000]-[0x0000] Range Decimal: [65136 to 1250]-[0]-[0]-[0] Hex: [0xFE70 to 0x04E2]-[0x0000]-[0x0000]-[0x0000]
150 | Motion RH Water Detect | u8 s16 s16 u8 | Motion Temperature Humidity Water | Motion detected/No motion detected Celsius (C) Relative Humidity (%) Water detected/No water detected | Default Mode: 0 = Motion/Water Detected 1 = No Motion/Water Detected Formulas: Temperature: Divide by 100 for 2 decimal resolution. Humidity: Divide by 100 for 2 decimal resolution. Examples: Temperature: 2162 / 100 = 21.62 C Humidity: 2401 / 100 = 24.01% | [Motion Detected]-[Temperature]-[Humidity]-[Water Detected] Example Decimal: [1]-[2162]-[2401]-[1] Hex: [0x0001]-[0x0872]-[0x0961]-[0x0001]
151 | 5 Input Dry Contact | u8 | Contact States | Integer | Default Mode: 0 = Contact Open 1 = Contact Closed Convert value to binary, each bit represents an individual contact: Example: 22 = 0001 0110 Byte: 000e dcba Bit0 (a) - Contact 1 Bit1 (b) - Contact 2 Bit2 (c) - Contact 3 Bit3 (d) - Contact 4 Bit4 (e) - Contact 5 Bit5-7 -Unused | [Contact States]-[NA]-[NA]-[NA] Example Decimal: [22]-[0]-[0]-[0] Hex: [0x0016]-[0x0000]-[0x0000]-[0x0000]
152 | Capacitive Level Sensor | s16 u32 | Level Capacitance | Percentage (%) Picofarads (pF) | Formulas: Percentage: Divide by 100 to get 2 decimal point resolution. Capacitance: Divide by 100 to get 2 decimal point resolution. Examples: Percentage: 9677 / 100 = 96.77% Capacitance: [1]+[27740] *Convert to hexadecimal* [0x0001]+[0x6C5C] = 0x00016C5C *Convert to decimal* 0x00016C5C = 93,276 Apply formula: 93,276 / 100 = 932.76 pF Range: Percent: 0.00% to 100.00% | [Level]-[Capacitance_H]-[Capacitance_L]-[NA] Example Decimal: [9677]-[1]-[27740]-[0] Hex: [0x25CD]-[0x0001]-[0x6C5C]-[0x0000]
153 | Dual Pulse Counter | u64 | Channel 1 | Pulses | Example: [0]+[1]+[53327]+[7879] *Convert to hexadecimal* [0x0000]+[0x0001]+[0xD04F]+[0x1EC7] = 0x00000001D04F1EC7 *Convert to decimal* 0x00000001D04F1EC7 = 7,789,813,447 pulses Range: 0 to 2^64-1 *Due to size limitations only Channel 1 can be read with the FRRs. To read Channel 2 data use Wireless Device Registers.* | [Count0]-[Count1]-[Count2]-[Count3] Example Decimal: [0]-[1]-[53327]-[7879] Hex: [0x0000]-[0x0001]-[0xD04F]-[0x1EC7]
154 | Resistive Bridge | u32 s16 | mV/V Temperature | millivolts/volt (mV/V) Celsius (C) | Formulas: mV/V: Divide by 100,000 to get 5 decimal point resolution. Temperature: Divide by 10 to get 1 decimal point resolution. Example: [305]+[16508] *Convert to hexadecimal* [0x0131]+[0x407C] = 0x01313E1C *Convert to decimal* 0x0131407C = 20,004,988 Apply Formula: 20,004,988 / 100,000 = 200.04988 mV/V Range: -1000.00000 to 1000.00000 mV/V | [mV/V_H]-[mV/V_L]-[Temperature]-[NA] Example Decimal: [305]-[16508]-[203]-[0] Hex: [0x0131]-[0x407C]-[0x00CB]-[0x0000]

## WD_Data Register Breakdown
Profile | Sensor Name | Data Type | Data Points Presented | Unit | Interpretation | Concatenation
The sensor profile number | Name of the sensor | Describes the base data type being generated by the sensor. *Each row correlates to its own data point | General description of the data present in the FRRs. | Units of measurement for each data point | Describes how to interpret the raw sensor data sent to the gateway. The data is stored in 16 bit Registers. Included is a breakdown of each register, any calculations required to convert the data to usable values, as well as the acceptable range of the sensor. | When receiving data larger than 16 bit format, concatenating registers will be required to reconstruct the original value. The concatenation order may change depending on sensor requirements; it is detailed below.
2 | Temperature | s16 | Temperature | Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C Data0 = Temperature Data1 - Data7 = NA | NA
3 | Dry Contact | u8 | Open/Closed | Integer | Default Mode: 0 = Open Loop 1 = Closed Loop Data0 = Open/Closed Data1 - Data7 = NA | NA
4 | Water Detect | u8 | Not Present / Present | Integer | Default Mode: 0 = Not Present 1 = Present Data0 = Not Present / Present Data1 - Data7 = NA | NA
5 | Activity Detection | u8 | Motion Detected / No Motion Detected | Integer | Default Mode: 0 = No Motion Detected 1 = Motion Detected Data0 = No Motion Detected / Motion Detected Data1 - Data7 = NA | NA
9 | Open/Closed | u8 | Open/Closed | Integer | Default Mode: 0 = Open Loop 1 = Closed Loop Data0 = Open/Closed Data1 - Data7 = NA | NA
11 | Button | u8 | Checking In / Pressed | Integer | 0 = Checking In 1 = Pressed Data0 = Checking In / Pressed Data1 - Data7 = NA | NA
12 | Control | u8 | Relay 1: On/Off; Relay 2: On/Off | Integer | 0 = Both Relays: OFF 1 = Relay 1: ON 2 = Relay 2: ON 3 = Both Relays: ON Data0 = RelayState Data1 - Data7 = NA | NA
15 | G-Force Snapshot | s16 s16 s16 | X-Axis Y-Axis Z-Axis | G-Force (G) G-Force (G) G-Force (G) | Formula: Divide by 1000 for 3 decimal resolution. Example: 2715 / 1000 = 2.715 Range: -8.000 G to 8.000 G Data0 = X-Axis Data1 = Y-Axis Data2 = Z-Axis Data3 - Data7 = NA | NA
16 | Impact | u8 | Force Detected / No Force Detected | Integer | Convert value to binary, each bit represents a different data point generated by the sensor. Definitions for each bit are listed below. Example: 187 = 1011 1011 Byte: hgfe dcba Bit0 (a) - X Polarity: 0 = g+ 1 = g- Bit1 (b) - X Event: 0 = none 1 = happened Bit2 (c) - Y Polarity: 0 = g+ 1 = g- Bit3 (d) - Y Event: 0 = none 1 = happened Bit4 (e) - Z Polarity: 0 = g+ 1 = g- Bit5 (f) - Z Event: 0 = none 1 = happened Bit6 (g) - EA: 0 = none 1 = Global Event happened Bit7 (h) - Internal Communication Problems Data0 = ForceDetection Data1 - Data7 = NA | NA
21
22 | 0-20 mA Current | u16 | Current | Milliamps (mA) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 744 / 100 = 7.44 mA Range: 0 mA to 24mA Data0 = Current Data1 - Data7 = NA
26
28
32
35 | High Temperature | s16 | Temperature | Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C Data0 = Temperature Data1 - Data7 = NA | NA
36
43 | Humidity | s16 s16 | Temperature Relative Humidity | Celcius (C) Relative Humidity (%) | Formula: Divide by 100 for 2 decimal resolution. Formula: Divide by 100 for 2 decimal resolution. Example: 2710 / 100 = 27.10 C, 4555 / 100 = 45.55% Range: -40.0 C to 125.0 C, 00.00% to 100.00% Data0 = Temperature Data1 = Humidity Data2 - Data7 = NA | NA
46 | Low Temperature | s16 | Temperature | Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -200.0 to 162.0 C Data0 = Temperature Data1 - Data7 = NA | NA
56 | H2S | s16 s16 s16 u16 | Temperature H2S Instant H2S TWA For Internal Use Only | Celcius (C) Parts Per Million (PPM) Parts Per Million (PPM) Integer | Formula: Divide by 10 for 1 decimal resolution. Formula: Divide by 1000 for 1 decimal resolution. Formula: Divide by 1000 for 1 decimal resolution. Example: 271 / 10 = 27.1 C 17800 / 1000 = 17.8 PPM Range: -40.0 C to 125.0 C Data0 = Temperature Data1 = H2S Instant Data2 = H2S TWA Data3 = For Internal Use Only Data4 - Data7 = NA | NA
59
64 | Voltage Detect 500VAC | u8 | No Voltage Present / Voltage Present | Integer | Default Mode: 0 = No Voltage Present 1 = Voltage Present Data0 = No Voltage Present / Voltage Present Data1 - Data 7 = NA | NA
65 | Water Temperature | s16 | Temperature | Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C Data0 = Temperature Data1 - Data7 = NA | NA
67 | Commercial Ultrasonic | u16 | Distance | Centimeters (CM) | Distance from target in CM. Range: 10 CM to 400 CM Data0 = Distance Data1 - Data7 = NA | NA
70 | Resistance | u32 | Resistance | Ohms (Ω) | Data produced by the sensor is in u32 format. 2 Registers are needed to contain this value. Concatenate the Registers in order to reconstruct the full value. Formula: Divide by 10 for 1 decimal point resolution Example: 2,471,234 / 10 = 247,123.4 Ω Range: 0 to 250,000.0 Ω Data0 = Resistance_L Data1 = Resistance_H Data2 - Data7 = NA | Resistance = [Data1]+[Data0] Example Data0 = 46402 Data1 = 37 Concatenate: [37]+[46402] *Convert to hexidecimal* [0x0025]+[0xB542] = 0x0025B542 *Convert to decimal* 0x0025B542 = 2,471,234 Apply Formula: 2,471,234 / 10 = 247,123.4 Resistance = 247,123.4 Ω
71
72 | 0-5 VDC | u16 | Voltage | Volts (V) | Formula: Divide by 1000 to get 1 decimal point resolution. Example: 3400 / 1000 = 3.4 V Range: 0 V to 5 V Data0 = Volts Data1 - Data7 = NA | NA
74 | 0-10 VDC | u16 | Voltage | Volts (V) | Formula: Divide by 1000 to get 1 decimal point resolution. Example: 7400 / 1000 = 7.4 V Range: 0 V to 10 V Data0 = Volts Data1 - Data7 = NA | NA
75 | Tilt | s16 s16 | Pitch Roll | Degrees (°) Degrees (°) | Formula: Divide by 100 for 2 decimal point resolution. Example: 17518 / 100 = 175.18° Range: -180.00° to 180.00° Data0 = Pitch Data1 = Roll Data2 - Data7 = NA | NA
78 | Water Rope | u8 | No Water Present / Water Present | Integer | Default Mode: 0 = No Water Present 1 = Water Present Data0 = No Water Present / Water Present Data1 - Data7 = NA | NA
79 | Pressure 50 | u16 | Pressure | Pounds/Square Inch (PSIG) | Formula: Divide by 10 to get 1 decimal point resolution. Example: 359 / 10 = 35.9 PSI Range: 0 PSI to 50 PSI Data0 = Pressure Data1 - Data7 = NA | NA
82 | Pressure 300 | u16 | Pressure | Pounds/Square Inch (PSIG) | Formula: Divide by 10 to get 1 decimal point resolution. Example: 2595 / 10 = 259.5 PSI Range: 0 PSI to 300 PSI Data0 = Pressure Data1 - Data7 = NA | NA
83 | Pressure Custom | u16 | Pressure | Pounds/Square Inch (PSIG) | Formula: Divide by 10 to get 1 decimal point resolution. Example: 359 / 10 = 35.9 PSI Range: 0 PSI to 50 PSI Data0 = Pressure Data1 - Data7 = NA | NA
84 | Duct Temperature | s16 | Temperature | Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C Data0 = Temperature Data1 - Data7 = NA | NA
86 | Thermocouple | s16 | Temperature | Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -100.0 to 400.0 C Data0 = Temperature Data1 - Data7 = NA | NA
90 | Pulse Counter(64) | u64 | Count | Pulses | Data produced by the sensor is in u64 format. 4 Registers are required to store this value. Concatenate the Registers in order to reconstruct the full value. Range: 0 to 2^64-1 Data0 = Count4 Data1 = Count3 Data2 = Count2 Data3 = Count1 Data4 - Data7 = NA | Count = [Data3]+[Data2]+[Data1]+[Data0] Example Data0 = 7879 Data1 = 53327 Data2 = 1 Data3 = 0 Concatenate: [0]+[1]+[53327]+[7879] *Convert to hexidecimal* [0x0000]+[0x0001]+[D04F]+[1EC7] = 0x00000001D04F1EC7 *Convert to decimal* 0x00000001D04F1EC7 = 7,789,813,447 Count = 7,789,813,447 Pulses
92 | Quad Temp | s16 s16 s16 s16 | Temperature Temperature Temperature Temperature | Celcius (C) Celcius (C) Celcius (C) Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C Data0 = Temperature1 Data1 = Temperature2 Data2 = Temperature3 Data3 = Temperature4 Data4 - Data7 = NA | NA
93 | Current Meter 20A | u64 u16 u16 u16 | Accumulate Avg Current Max Current Min Current | Amp Hours (Ah) Amps (A) Amps (A) Amps (A) | Data produced by the sensor is in multiple formats. 4 Registers are required to store the u64 value. Concatenate the registers in order to reconstruct the full value. Apply formula after concatenation. Formula: Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A/Ah Range: 0 A to 50 A *Physical hardware limitations* Data0 = Acc4 Data1 = Acc3 Data2 = Acc2 Data3 = Acc1 Data4 = AvgCurrent Data5 = MaxCurrent Data6 = MinCurrent Data7 = NA | Accumulate = [Data3]+[Data2]+[Data1]+[Data0] Example Data0 = 21847 Data1 = 520 Data2 = 0 Data3 = 0 Concatenate: [0]+[0]+[520]+[21847] *Convert to hexidecimal* [0x0000]+[0x0000]+[0x0208]+[0x5557] = 0x0000000002085557 *Convert to decimal* 0x0000000002085557 = 34,100,567 Apply Formula: 34,100,567 / 100 = 341,005.67 Accumulate = 341,005.67 Ah
94 | Current Meter 150A | u64 u16 u16 u16 | Accumulate Avg Current Max Current Min Current | Amp Hours (Ah) Amps (A) Amps (A) Amps (A) | Data produced by the sensor is in multiple formats. 4 Registers are required to store the u64 value. Concatenate the registers in order to reconstruct the full value. Apply formula after concatenation. Formula: Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A/Ah Range: 0 A to 200 A *Physical hardware limitations* Data0 = Acc4 Data1 = Acc3 Data2 = Acc2 Data3 = Acc1 Data4 = AvgCurrent Data5 = MaxCurrent Data6 = MinCurrent Data7 = NA | Accumulate = [Data3]+[Data2]+[Data1]+[Data0] Example Data0 = 21847 Data1 = 520 Data2 = 0 Data3 = 0 Concatenate: [0]+[0]+[520]+[21847] *Convert to hexidecimal* [0x0000]+[0x0000]+[0x0208]+[0x5557] = 0x0000000002085557 *Convert to decimal* 0x0000000002085557 = 34,100,567 Apply Formula: 34,100,567 / 100 = 341,005.67 Accumulate = 341,005.67 Ah
95 | Vibration Meter | u8 u8 u8 u8 u8 u8 u8 | X Speed Y Speed Z Speed X MaxFreq Y MaxFreq Z MaxFreq Duty Cycle | Millimeters Per Second (MM/S) Millimeters Per Second (MM/S) Millimeters Per Second (MM/S) Hertz (Hz) Hertz (Hz) Hertz (Hz) Percentage (%) | Formulas Speed: Divide by 10 for 1 decimal resolution. Frequency: No calculation required. Duty Cycle: No calculation required. Example: 235 / 10 = 23.5 mm/s Range: 0 to 255, 0 to 255, 0 to 100 Data0_L = X Speed (u8) Data0_H = Y Speed (u8) Data1_L = Z Speed (u8) Data1_H = X MaxFreq Data2_L = Y MaxFreq Data2_H = Z Max Freq Data3_L = Duty Cycle Data3_H = NA Data4 - Data7 = NA | X Speed = [Data0_L] Y Speed = [Data0_H] Z Speed = [Data1_L] X MaxFreq = [Data1_H] Y MaxFreq = [Data2_L] Z maxFreq = [Data2_H] Duty Cycle = [Data3_L] Example Data0 = 1250 --> Convert to hexidecimal --> [0x04E2] Data1 = 10456 --> Convert to hexidecimal --> [0x28D8] Data2 = 7123 --> Convert to hexidecimal --> [0x1BD3] Data3 = 75 --> Convert to hexidecimal --> [0x004B] Concatenate: Data3 Data2 Data1 Data0 [0x004B]+[0x1BD3]+[0x28D8]+[0x04E2] = 0x00941BD328D804E2 -> BreakOut into bytes D3_H D3_L D2_H D2_L D1_H D1_L D0_H D0_L [0x00] [0x4B] [0x1B] [0xD3] [0x28] [0xD8] [0x04] [0xE2] --> Convert to decimal Apply Formula: X Speed = 226/10 = 22.6 mm/s Y Speed = 4/10 = 0.4 mm/s Z Speed = 216/10 = 21.6 mm/s X MaxFreq = 40 Hz Y MaxFreq = 211 Hz Z MaxFreq = 27 Hz Duty Cycle = 75%
97 | Thermostat | s16 s16 u8 | Temerature Humidity State | Celcius (C) Relative Humidity (%) Integer | Formula: Divide by 100 for 2 decimal resolution. Formula: Divide by 100 for 2 decimal resolution. Covert to Binary to identify what states are active. Each bit corresponds to an individual state. See State/Bit definitions below. Example: 2710 / 10 = 27.10 C, 4555 / 100 = 45.55%, 13 = 0000 1101 (LSV) Bit0 - Heater State 0 = OFF / 1 = ON Bit1 - Cooler State 0 = OFF / 1 = ON Bit2 - Fan State 0 = OFF / 1 = ON Bit3 - Occupancy State 0 = OFF / 1 = ON Bit4 - Fan Override 0 = OFF / 1 = ON Bit5 - Occupied Overried 0 = OFF / 1 = ON Bit6 - Unoccupied Overried 0 = OFF / 1 = ON (MSV) Bit7 - Settings Lockout 0 = OFF / 1 = ON Range: -40.0 C to 85.0 C, 00.00% to 100.00%, 0 to 255 Data0 = Temperature Data1 = Humidity Data2 = State Data3 - Data7 = NA | NA
98
100
101 | PIR | u8 | Motion Detected / No Motion Detected | Integer | Default Mode: 0 = No Motion Detected 1 = Motion Detected Data0 = NoMotion / Motion Data1 - Data7 = NA | NA
102 | Air Quality | u16 u16 u16 u8 | PM 1 PM 2.5 PM 10 For Internal Use Only | Micrograms/meter cubed (ug/m^3) Micrograms/meter cubed (ug/m^3) Micrograms/meter cubed (ug/m^3) Integer | No conversion required. Range: 0 to 1000 ug/m^3 Data0 = PM1_0 Data1 = PM2_5 Data2 = PM10 Data3 = For Internal Use Only Data4 - Data7 = NA | NA
103 | Differential Pressure | s16 s16 | Pressure Temperature | Pascals (Pa) Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Formula: Divide by 10 for 1 decimal resolution. Example: 2710 / 10 = 271.0 Pa, 455 / 10 = 45.5 C Range: -500 to 500 Pa, -40.0 C to 125.0 C Data0 = Pressure Data1 = Temperature Data2 - Data7 = NA | NA
105 | Industrial Ultrasonic | u16 | Distance | Centimeters (CM) | Distance from target in CM. Range: 20 CM to 750 CM Data0 = Distance Data1 - Data7 = NA | NA
106 | C02 Meter | s16 s16 s16 s16 | Avg C02 TWA C02 For Internal Use Only For Internal Use Only | Parts Per Million (PPM) Parts Per Million (PPM) Integer Integer | Displays C02 in parts per million. Example: C02 Instantaneous: 2710 PPM, C02 TWA: 100 PPM Range: 0 to 10,000 PPM, 0 to 10,000 PPM Data0 = Avg C02 Data1 = TWA C02 Data2 = For Internal Use Only Data3 = For Internal Use Only Data4 - Data7 = NA | NA
107 | Light Meter | u32 u8 | Intensity Light/No Light | Luminescence/unit area (LUX) Integer | Data produced by the sensor is in multiple formats. The u32 value requires 2 Registers in order to contain this data. Concatenate the Registers in order to reconstruct the full value. Formula: Divide by 100 for 2 decimal point resolution Example: 94,531 / 100 = 945.31 LUX Range: 0 - 1000 LUX, 0 = No Light / 1 = Light Data0 = Intensity_L Data1 = Intensity_H Data2 = NoLight / Light Data3 - Data7 = NA | Intensity = [Data1]+[Data0] Example Data0 = 28995 Data1 = 1 Concatenate: [1]+[28995] *Convert to hexidecimal* [0x0001]+[0x7143] = 0x00017143 *Convert to decimal* 0x00017143 = 94,531 Apply Formula: 94,531 / 100 = 945.31 Intensity = 945.31 LUX
109 | Three Phase 150A | u16 u8 u8 u8 u16 u8 u8 u8 u16 u8 u8 u8 u32 | Phase1 AvgCurrent Phase1 MaxCurrent Phase1 MinCurrent Phase1 DutyCycle Phase2 AvgCurrent Phase2 MaxCurrent Phase2 MinCurrent Phase2 DutyCycle Phase3 AvgCurrent Phase3 MaxCurrent Phase3 MinCurrent Phase3 DutyCycle Accumulate | Amps (A) Amps (A) Amps (A) Percentage (%) Amps (A) Amps (A) Amps (A) Percentage (%) Amps (A) Amps (A) Amps (A) Percentage (%) Amp Hours (Ah) | *This sensor produces more data than what can be stored in the 8 available Registers. The data is produced in multiple formats. Omitted data will only be accessable through a different gateway type. Formula: u8 Data - No calculation required. u16 Data - Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A Range: 0 A to 200 A *Physical hardware limitations for each phase* Data0 = Phase1 AvgCurrent (u16) Data1_L = Phase1 MaxCurrent (u8) Data1_H = Phase1 MinCurrent (u8) Data2 _L= Phase1 DutyCycle (u8) Data2_H = Phase2 AvgCurrent_L (u8) Data3_L = Phase2 AvgCurrent_H (u8) Data3_H = Phase2 MaxCurrent (u8) Data4_L = Phase2 MinCurrent (u8) Data4_H = Phase2 DutyCylce (u8) Data5 = Phase3 AvgCurrent (u16) Data6_L = Phase3 MaxCurrent (u8) Data6_H = Phase3 MinCurrent (u8) Data7_L = Phase3 DutyCycle (u8) Data7_H = Accumulate1 (u8) *Limited use case, up to 25.5 Ah* | Phase2 AvgCurrent = [Data3_L]+[Data2_H] Example Data2 = 29560 --> Convert to hexidecimal --> 0x7378 Data3 = 12833 --> Convert to hexidecimal --> 0x3221 1st Concatenate: [0x3221]+[0x7378] = 0x32217378 --> BreakOut into bytes [0x32] [0x21] [0x73] [0x78] -------> [0x32] [0x21]+[0x73] [0x78] Data3 Data2 ReOrder Data3_L+Data2_H 2nd Concatenate: [0x32] [0x21]+[0x73] [0x78] = [0x32] [0x2173] [0x78] --> Convert to decimal [50] [8563] [120] Apply Formula: Phase1 Duty Cycle - 50% Phase2 AvgCurrent - 8563 / 100 = 85.63 A Phase2 MaxCurrent - 120 A
111 | Advanced Vibration | u8 u16 u16 u16 u16 u16 u16 u8 u8 u8 u8 s16 | Mode X Frequency Y Frequency Z Frequency X Vibration Y Vibration Z Vibration X CrestFactor Y CrestFactor Z CrestFactor Duty Cycle Temperature | Integer Hertz (Hz) Hertz (Hz) Hertz (Hz) mm/s^2 OR mm/s OR mm mm/s^2 OR mm/s OR mm mm/s^2 OR mm/s OR mm Integer Integer Integer Percentage (%) Celsius (C) | *This sensor produces more data than what can be stored in the available 8 Registers. The omitted data may only be accessable through the FRR data or a different type of gateway. Vibration can be configured to measure in Acceleration, Velocity, or Displacement and this will determing the units of measurement. Formulas Mode: 0 = Velocity RMS, 1 = Acceleration RMS, 4 = Displacement RMS. Frequency: Divide by 5 for 1 decimal point resolution. Vibration (Velocity): Divide by 100 for 2 decimal point resolution. Vibration (Acceleration): Multiply by 10 for integer resolution. Vibration (Displacement): Divide by 100 for 2 decimal point resolution. Crest Factor: Divide by 100, then Add 1.41 for 2 decimal point resolution. Duty Cycle: Not enough room to contain this data. Temperature: Not enough room to contain this data. Example Range Frequency: 24863 / 5 = 497.2 Hz 0 to 65535 Velocity: 24863 / 100 = 248.63 mm/s 0 to 65535 Acceleration: 24863 * 10 = 2486.30 mm/s^2 0 to 65535 Displacement: 24863 / 100 = 248.63 mm 0 to 65535 Crest Factor: (245 / 100)+1.41 = 2.86 0 to 255 Data0_L = Mode (u8) Data4_L = XVibe_H (u8) Data0 _H = XFreq_L (u8) Data4_H = YVibe_L (u8) Data1_L = XFreq_H (u8) Data5_L = YVibe_H (u8) Data1_H = YFreq_L (u8) Data5_H = ZVibe_L (u8) Data2_L = YFreq_H (u8) Data6_L = ZVibe_H (u8) Data2_H = ZFreq_L (u8) Data6_H = XCrestFactor (u8) Data3_L = ZFreq_H (u8) Data7_L = YCrestFactor (u8) Data3_H = XVibe_L (u8) Data7_H = ZCrestFactor (u8) | X Frequency = [Data1_L]+[Data0_H] Y Frequency = [Data2_L]+[Data1_H] Z Frequency = [Data3_L]+[Data2_H] X Vibration = [Data4_L]+[Data3_H] Y Vibration = [Data5_L]+[Data4_H] Z Vibration = [Data6_L]+[Data5_H] Example Data0 = 11520 --> Convert to hexidecimal --> 0x2D00 Data1 = 11521 --> Convert to hexidecimal --> 0x2D01 Data2 = 11521 --> Convert to hexidecimal --> 0x2D01 Data3 = 55297 --> Convert to hexidecimal --> 0xD801 Data4 = 55812 --> Convert to hexidecimal --> 0xDA04 Data5 = 62210 --> Convert to hexidecimal --> 0xF302 Data6 = 8961 --> Convert to hexidecimal --> 0x2301 Data7 = 17692 --> Convert to hexidecimal --> 0x451C 1st Concatenate: D7 D6 D5 D4 D3 D2 D1 D0 [0x451C]+[0x2301]+[0xF302]+[0xDA04]+[0xD801]+[0x2D01]+[0x2D01]+[0x2D00] = 0x451C2301F302DA04D8012D012D012D00 --> BreakOut into bytes D7 D6 D5 D4 D3 D2 D1 D0 [45][1C] [23][01] [F3][02] [DA][04] [D8][01] [2D][01] [2D][01] [2D][00] H L H L H L H L H L H L H L H L 2nd Concatenate: D7 D7 D6 D6 D5 D5 D4 D4 D3 D3 D2 D2 D1 D1 D0 D0 [45] [1C] [23] [01]+[F3] [02]+[DA] [04]+[D8] [01]+[2D] [01]+[2D] [01]+[2D] [00] H L H L H L H L H L H L H L H L Mode = [0x00] --> Convert to decimal --> 0 (Velocity) X Frequency = [0x012D] --> Convert to decimal, apply formula --> 301/5 = 60.2 Hz Y Frequency = [0x012D] --> Convert to decimal, apply formula --> 301/5 = 60.2 Hz Z Frequency = [0x012D] --> Convert to decimal, apply formula --> 301/5 = 60.2 Hz X Vibration = [0x04D8] --> Convert to decimal, apply formula --> 1240/100 = 12.40 mm/s Y Vibration = [0x02DA] --> Convert to decimal, apply formula --> 730/100 = 7.30 mm/s Z Vibration = [0x01F3] --> Convert to decimal, apply formula --> 499/100 = 4.99 mm/s X CrestFactor = [0x23] --> Convert to decimal, apply formula --> (35/100)+1.41 = 1.76 CF Y CrestFactor = [0x1C] --> Convert to decimal, apply formula --> (28/100)+1.41 = 1.69 CF Z CrestFactor = [0x45] --> Convert to decimal, apply formula --> (69/100)+1.41 = 2.10 CF
113 | Voltage Meter 200VDC | u32 | Voltage | Volts (V) | Data produced by the sensor is in u32 format. 2 Registers are needed to contain this value. Concatenate the Registers in order to reconstruct the full value. Formula: Divide by 100 for 2 decimal point resolution Range: 0 - 250 V *Physical hardware limitations* Data0 = Voltage1 Data1 = Voltage2 Data2 - Data7 = NA | Voltage = [Data0]+[Data1] Example Data0 = 0 --> Convert to hexidecimal --> 0x0000 Data1 = 19873 --> Convert to hexidecimal --> 0x4DA1 Concatenate: [0x0000]+[0x4DA1] = 0x00004DA1 --> Convert to decimal --> 19873 Apply Formula: 19873 / 100 = 198.73 Voltage = 198.73 V
114 | Air Velocity | s16 s16 | Velocity Temperature | Meters Per Second (M/S) Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 176 / 10 = 17.6 m/s, 271 / 10 = 27.1 C Range: 0 to 50 m/s, -40.0 C to 125.0 C NOTE: Velocity range will change based on altitude. 0M = 0-30 m/s, 5000M = 0-40 m/s, 8000M = 0-50 m/s Data0 = Velocity Data1 = Temperature Data2 - Data7 = NA | NA
116 | C0 Meter | u16 u16 u16 u16 | Temperature Instant C0 TWA C0 For Internal Use Only | Celcius (C) Parts Per Million (PPM) Parts Per Million (PPM) Integer | Formula: Divide by 10 for 1 decimal resolution. Formula: Divide by 10 for 1 decimal resolution. Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40 to 125 C, 0 to 1000 PPM, 0 to 1000 PPM Data0 = Temperature Data1 = Instant C0 Data2 = TWA C0 Data3 = For Internal Use Only Data4 - Data 7 = NA | NA
119 | Car Detect | u8 u16 | Mode Indicator Car Count | Integer Integer | Identifies which mode the sensor is currently operating in. 0 = No Car Detected 1 = Car Detected (Trigger Modes), 2 = Count Mode Counts the numbers of cars detected within a user configured timeframe. Range: 0-2, 0-65535 Data0_H = CarCount_L(u8) Data0_L = Mode(u8) Data1 = CarCount_H(u8) | Mode = [Data0_L] Car Count = [Data1]+[Data0_H] Example Data0 = 11266 --> Convert to hexidecimal --> 0x2C02 Data1 = 1 --> Convert to hexidecimal --> 0x0001 Concatenate: [0x0001]+[0x2C02]= 0x00012C02 [Data1]+[Data0_H] = [0x00 01] [2C] or [0x012C] --> Convert to deicimal --> 300 [Data0_L] = [0x02] --> Convert to Decimal --> 2 Mode = 2 Car Count = 300
120 | Current Meter 500A | u64 u16 u16 u16 | Accumulate Avg Current Max Current Min Current | Amp Hours (Ah) Amps (A) Amps (A) Amps (A) | Data produced by the sensor is in multiple formats. 4 Registers are required to store the u64 value. Concatenate the registers in order to reconstruct the full value. Apply formula after concatenation. Formula: Divide by 100 to get 2 decimal point resolution. Example: 1567 / 100 = 15.67 A/Ah Range: 0 A to 600 A *Physical hardware limitations* Data0 = Acc4 Data1 = Acc3 Data2 = Acc2 Data3 = Acc1 Data4 = AvgCurrent Data5 = MaxCurrent Data6 = MinCurrent Data7 = NA | Accumulate = [Data3]+[Data2]+[Data1]+[Data0] Example Data0 = 21847 Data1 = 520 Data2 = 0 Data3 = 0 Concatenate: [0]+[0]+[520]+[21847] *Convert to hexidecimal* [0x0000]+[0x0000]+[0x0208]+[0x5557] = 0x0000000002085557 *Convert to decimal* 0x0000000002085557 = 34,100,567 Apply Formula: 34,100,567 / 100 = 341,005.67 Accumulate = 341,005.67 Ah
122 | Voltage Meter 500VAC | u16 | Voltage | Volts (V) | Formula: Divide by 100 to get 2 decimal point resolution. Example: 15670 / 100 = 156.70 A Range: 0 A to 600 A *Physical hardware limitations* Data0 = Volts Data1 - Data7 = NA | NA
123 | Voltage Detect 200VDC | u8 | No Voltage Present / Voltage Present | Integer | Default Mode: 0 = No Voltage Present 1 = Voltage Present Data0 = No Voltage Present / Voltage Present Data1 - Data 7 = NA | NA
124 | Propane | s16 u16 | Gas Level Voltage | Percentage (%) Millivolts (mV) | How much gas is remaining in the tank. Hall Effect reading expresed as mV. Formula: Divide by 100 for 2 decimal resolution. Range: 0-100, 0-5000 Data0 = Gas Level Data1 = Voltage Data2 - Data7 = NA | NA
126 | Accelerometer Max/Avg | u16 u16 u16 u16 u16 u16 u16 u16 | X Max Y Max Z Max Max Magnitude X Avg Y Avg Z Avg Avg Magnitude | G-Force (G) G-Force (G) G-Force (G) G-Force (G) G-Force (G) G-Force (G) G-Force (G) G-Force (G) | Formula: Divide by 1000 for 3 decimal resolution. Example: 7856 / 1000 = 7.856 G Range: 0.000 to 8.000 G Data0 = X Max Data1 = Y Max Data2 = Z Max Data3 = Max Magnitude Data4 = X Avg Data5 = Y Avg Data6 = Z Avg Data7 = Avg Magnitude | NA
129 | Three Phase 500A | u16 u8 u8 u8 u16 u8 u8 u8 u16 u8 u8 u8 u32 | Phase1 AvgCurrent Phase1 MaxCurrent Phase1 MinCurrent Phase1 DutyCycle Phase2 AvgCurrent Phase2 MaxCurrent Phase2 MinCurrent Phase2 DutyCycle Phase3 AvgCurrent Phase3 MaxCurrent Phase3 MinCurrent Phase3 DutyCycle Accumulate | Amps (A) Amps (A) Amps (A) Percentage (%) Amps (A) Amps (A) Amps (A) Percentage (%) Amps (A) Amps (A) Amps (A) Percentage (%) Amp Hours (Ah) | *This sensor produces more data than what can be stored in the 8 available Registers. The data is produced in multiple formats. Omitted data will only be accessable through a different gateway type. Formula: u8 DutyCycle Data - No calculation required. u8 Data - Multiply by 3 for integer resolution. u16 Data - Divide by 100 to get 2 decimal point resolution. u32 Data - Divide by 10 for 1 decimal point resolution. Example: 1567 / 100 = 15.67 A, 120 * 3 = 360 A Range: 0 A to 600 A *Physical hardware limitations for each phase* Data0 = Phase1 AvgCurrent (u16) Data1_L = Phase1 MaxCurrent (u8) Data1_H = Phase1 MinCurrent (u8) Data2 _L= Phase1 DutyCycle (u8) Data2_H = Phase2 AvgCurrent_L (u8) Data3_L = Phase2 AvgCurrent_H (u8) Data3_H = Phase2 MaxCurrent (u8) Data4_L = Phase2 MinCurrent (u8) Data4_H = Phase2 DutyCylce (u8) Data5 = Phase3 AvgCurrent (u16) Data6_L = Phase3 MaxCurrent (u8) Data6_H = Phase3 MinCurrent (u8) Data7_L = Phase3 DutyCycle (u8) Data7_H = Accumulate1 (u8) *Limited use case, up to 25.5 Ah* | Phase2 AvgCurrent = [Data3_L]+[Data2_H] Example Data2 = 29560 --> Convert to hexidecimal --> 0x7378 Data3 = 12833 --> Convert to hexidecimal --> 0x3221 1st Concatenate: [0x3221]+[0x7378] = 0x32217378 --> BreakOut into bytes [0x32] [0x21] [0x73] [0x78] -------> [0x32] [0x21]+[0x73] [0x78] Data3 Data2 ReOrder Data3_L+Data2_H 2nd Concatenate: [0x32] [0x21]+[0x73] [0x78] = [0x32] [0x2173] [0x78] --> Convert to decimal [50] [8563] [120] Apply Formula: Phase1 Duty Cycle - 50% Phase2 AvgCurrent - 8563 / 100 = 85.63 A Phase2 MaxCurrent - 120 * 3 = 360 A
130 | Accelerometer Tilt Detect | (s16) (s16) (s8) | Pitch Actuation Time State | Degrees milliseconds N/A | Formula: Divide by 100 for 2 decimal resolution. Example: 150 / 100 = 1.50 degrees Range: -179.99 thru +180.00 Actuation Time is in ms. State is used as is and represents the following in Up/Down mode: 0 - Down, 1 - UP, 2 - Stuck State is used as is and represents the following in Delta mode: 0 - not triggered, 1 - delta change triggered | NA
131 | Filtered Quad Temp | s16 s16 s16 s16 | Temperature Temperature Temperature Temperature | Celcius (C) Celcius (C) Celcius (C) Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C Data0 = Temperature1 Data1 = Temperature2 Data2 = Temperature3 Data3 = Temperature4 Data4 - Data7 = NA | NA
132 | Filtered Temperature | s16 | Temperature | Celcius (C) | Formula: Divide by 10 for 1 decimal resolution. Example: 271 / 10 = 27.1 C Range: -40.0 to 125.0 C Data0 = Temperature Data1 - Data7 = NA | NA
150 | Motion RH Water Detect | u8 u16 u16 u8 | Motion Temperature Humidity Water | Motion detected/No motion detected Celsius (C) Relative Humidity (%) Water detected/No water detected | Default Mode: 0 = Motion/Water Detected 1 = No Motion/Water Detected Formulas: Temperature: Divide by 100 for 2 decimal resolution. Humidity: Divide by 100 for 2 decimal resolution. Examples: Temperature: 2162 / 100 = 21.62 C Humidity: 2401 / 100 = 24.01% Data0_L = Motion Detection Data0_H = Temperature_L Data1_L = Temperature_H Data1_H = Humidity_L Data2_L = Humidity_H Data2_H = Water Detection Data3 - Data7 = NA | Temperature = [Data1_L]+[Data0_H] Humidity = [Data2_L]+[Data1_H] Example Data0 = 29185 --> Convert to hexidecimal --> 0x7201 Data1 = 24840 --> Convert to hexidecimal --> 0x6108 Data2 = 9 --> Convert to hexidecimal --> 0x0009 1st Concatenate: Data2 Data1 Data0 [0x0009] + [0x6108] + [0x7201] --> BreakOut into bytes [0x00] [0x09] [0x61] [0x08] [0x72] [0x01] 2nd Concatenate: [0x00] [0x09]+[0x61] [0x08]+[0x72] [0x01] = [0x00] [0x0961] [0x0872] [0x01] --> Convert to decimal [0] [2401] [2162] [1] Apply Formulas: Motion Detection = Detected Temperature: 2162/100 = 21.62 C Humidity = 2401/100 = 24.01% Water Detection = Not Detected
151 | 5 Input Dry Contact | u8 u8 u8 u8 u8 | Contact 1 Contact 2 Contact 3 Contact 4 Contact 5 | Integer Integer Integer Integer Integer | Default mode: 0 = Contact Open 1 = Contact Closed Data0_L = Contact 1(u8) Data1_L = Contact 2(u8) Data2_L = Contact 3(u8) Data3_L = Contact 4(u8) Data4_L = Contact 5(u8) Data4_H - Data7 = NA | NA
152 | Capacitive Level Sensor | s16 u32 | Level Capacitance | Percentage (%) Picofarads (pF) | Formulas: Percentage: Divide by 100 to get 2 decimal point resolution. Capacitance: Divide by 100 to get 2 decimal point resolution. Range: 0.00% to 100.0% Data0 = Level Data1 = Capacitance_H Data2 = Capacitance_L Data3 - Data7 = NA | Capacitance = [Data1]+[Data2] Example Data1 = 1 Data2 = 27740 Concatenate: [1]+[27740] *Convert to hexidecimal* [0x0001]+[0x6C5C] = 0x00016C5C *Convert to decimal* 0x00016C5C = 93276 Apply Formula: 93,276 / 100 = 932.76 Capacitance = 932.76 pF
153 | Dual Pulse Counter | u64 u64 | Channel 1 Channel 2 | Pulses Pulses | Data produced by the sensor is in u64 format. 4 Registers are required to store this value. Concatenate the Registers in order to reconstruct the full value. Range: 0 to 2^64-1 Data0 = Channel 1 Count1 (LSB) Data1 = Channel 1 Count2 Data2 = Channel 1 Count3 Data3 = Channel 1 Count4 (MSB) Data4 = Channel 2 Count1 (LSB) Data5 = Channel 2 Count2 Data6 = Channel 2 Count3 Data7 = Channel 2 Count4 (MSB) | Channel 1 Count = [Data3]+[Data2]+[Data1]+[Data0] Channel 2 Count = [Data7]+[Data6]+[Data5]+[Data4] Example Data0 = 19556 Data1 = 7879 Data2 = 8 Data3 = 0 Data4 = 50113 Data5 = 19555 Data6 = 1 Data7 = 0 Concatenate: [0]+[8]+[7879]+[19556] *Convert to hexidecimal* [0x0000]+[0x0008]+[0x1EC7]+[0x4C64] = 0x000000081EC74C64 *Convert to decimal* 0x000000081EC74C64 = 34,876,116,068 [0]+[1]+[19555]+[50113] *Convert to hexidecimal* [0x0000]+[0x0001]+[0x4C63]+[0xC3C1] = 0x000000014C63C3C1 *Convert to decimal* 0x000000014C63C3C1 = 5,576,573,889 Channel 1 Count = 34,876,116,068 Pulses Channel 2 Count = 5,576,573,889 Pulses
154 | Resistive Bridge | u32 s16 | mV/V Temperature | millivolts/volt (mV/V) Celsius (C) | Formulas: mV/V: Divide by 100,000 to get 5 decimal point resolution. Temperature: Divide by 10 to get 1 decimal point resolution. Range: -1000 to 1000 mV/V Data0 = mV/V_L Data1 = mV/V_H Data2 = Temperature Data3 - Data7 = NA | mV/V = [Data1]+[Data0] Example Data1 = 305 Data0 = 16508 Concatenate: [305]+[16508] *Convert to hexidecimal* [0x0131]+[0x407C] = 0x01313E1C *Convert to decimal* 0x0131407C = 20,004,988 Apply Formula: 20,004,988 / 100,000 = 200.04988 mV/V = 200.04988